- SECTION 21 12 00

- STANDPIPE SUPERVISORY SYSTEM

- PART 1 - GENERAL

  - SUMMARY

    - Section includes: Standpipe supervisory system.

    - Related sections:

      - 21 12 00 Fire Suppression Standpipes

      - 01 43 00 Quality Control.

      - 21 05 00 Common Work Results for Fire Suppression.

      - 21 06 00 Schedules for Fire Suppression.

      - Drawings and general provisions of the contract, including General and Supplementary Conditions and Division 01 Specification Sections.

  - REFERENCES

    - All requirements of the Fire Department of the City of New York.

    - City of New York Local Law 64 of 2009.

    - Building Code of the City of New York Section 3303.8.1.

    - NYC Department of Buildings Bulletin – “New Standpipe Air Pressurized Alarm Requirements”.

  - SYSTEM DESCRIPTION

    - Furnish and install a self-contained and pre-assembled standpipe supervisory system that contains all mechanical and electrical components required.  The assembly shall be STANDPIPE-PAC™ Model SSS-100, manufactured by United Fire Systems, Kenilworth, NJ (908-688-0300, x222).

    - The assembly shall be pre-assembled, pre-wired, and fully factory tested as a system.

  - PERFORMANCE REQUIREMENTS

    - General.

      - Design and performance of systems, components, and methods specified herein shall comply with all applicable referenced codes and standards.

      - Contract drawings indicate the general arrangement of the system and are a guide for intent only.  Contractor is responsible for providing and installing all equipment necessary to complete the installation in compliance with all applicable requirements.

      - Contractor shall design, furnish, and install the standpipe supervisory system(s) per this specification, and shall provide Professional Engineering services needed to assume Engineering responsibility.

      - All piping system components shall be approved for at least 175 PSIG working pressure.

      - Power Requirements.

        - Primary.  Primary power shall be from a 110VAC dedicated branch circuit.

        - Standby.  Standby power for the control panel shall be provided by a rechargeable gel-cell battery installed in the STANDPIPE-PAC™ control panel enclosure.

    - System Operation.  The system shall operate in accordance with Section 4 of New York City Local Law 64 of 2009.  In addition, the following items shall be included:

      - The audible device shall be silenceable at the control panel.

      - A separate trouble signal shall be generated by trouble on any supervised circuit.

      - Battery shall be capable of powering the control panel in the event of AC power loss.  The battery shall be kept charged by the power supply of the control panel.

      - A built-in digital communicator shall annunciate signals to the site safety office or to a central station.

  - QUALITY ASSURANCE

    - Perform a level of Quality Control in accordance with Section 01 43 00.

    - Furnish a Quality Work Plan per Section 01 43 00 for this work.

    - Shop drawings and design calculations shall include a seal and signature by a qualified Licensed Professional Engineer, registered in New York State.

  - SUBMITTALS

    - Action Submittals.

      - Product Data.  For STANDPIPE-PAC™ product, include, as applicable, product rated capacities, operational characteristics, electrical characteristics, materials of construction, standards of construction, and approvals.

      - Shop Drawings.  Include all pertinent information.

        - An electrical riser diagram, specific to this design, showing interconnection of all electrical devices.

        - A mechanical riser diagram specific to this design, showing interconnection of all mechanical devices.

        - Wiring diagrams for all electrical devices and power, signal, and control wiring.

    - Delegated-Design Submittals.  Include performance requirements and design criteria analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

    - Information Submittals.

      - Qualification Data.

        - Installing Contractor.

        - Professional Engineer.

    - Commissioning Submittal: Field Test Plan.

    - Closeout Submittal: As-Built Drawing.

    - Operation and Maintenance Submittals: Instructions for STANDPIPE-PAC™.

- PART 2 - PRODUCTS

  - STANDPIPE SUPERVISORY SYSTEM. Furnish and install factory-wired and factory-tested self-contained standpipe supervisory system containing all mechanical and electrical components required.  The assembly shall be STANDPIPE-PAC™ Model SSS-100, manufactured by United Fire Systems, Kenilworth, NJ USA (908-688-0300 x222), and shall contain all components factory-assembled and tested to make up a complete, ready-to-install device  The assembly shall consist of:

    - A painted plywood backplane to which the following devices are securely attached:

      - Compressor to provide supervisory pressure factory assembled, wired and attached to system outlet.

        - Compressor shall be sized to permit filling of standpipe to minimum 11 PSIG in 2 hours or less.

        - Compressor shall be of the oil-less piston type, equipped with a pressure switch and a bubble-tight check valve.

        - Power: 110 VAC 60 Hz, 1 phase, controlled through a manual on / off switch.

      - All necessary pressure switches for signaling and compressor control.

        - Switch that operates when pressure in standpipe drops below supervisory pressure.  Switch contact factory-connected to control panel input circuit.

        - Switch that operates when pressure in standpipe exceeds 25 PSIG.  Switch contact factory-connected to control panel input circuit

        - Switch integral to compressor that cuts in at 13 PSIG and cuts out at 18 PSIG.  Switch contacts factory-connected to compressor power circuit.

      - Air dryer.

      - Control panel for signaling and notification functions, factory wired to signaling pressure switches and audible horn.  In addition control panel shall:

        - Include digital communicator for site safety office and /or central station notification.

        - Supervise and charge control panel backup battery, and shall automatically switch to backup power, in the event AC power is lost.

      - Audible horn.

      - Pressure gage for local indication.

      - Lockable shutoff valve.

      - Check valve to prevent water from entering device.

      - 120VAC, 60 Hz, single phase connection point to serve both control panel and compressor.

      - Pipe, fittings, fasteners, wire, raceway, and boxes factory assembled for complete interconnection of all items.  No field assembly permitted.

    - A separate manual air release angle valve with label to be field installed.

  - PIPE AND FITTINGS.  Pipe and fittings for connection of STANDPIPE-PAC™ to standpipe.

    - Pipe – Schedule 40 Steel, per ASTM A53 / A53M – Specification for Pipe, Steel, Black, Welded and Seamless.

    - Nipples – Steel Pipe Nipples, Threaded End, per ASTM A733 – Specification for Welded and Seamless Carbon Steel Pipe Nipples.

    - Fittings – All fittings shall be black.  Galvanized fittings shall not be painted.  Fittings per ANSI B16.3 – Malleable Iron Threaded Fittings, or ANSI B16.4 – Cast Iron Threaded Fittings.

    - Couplings – Per ASTM A 865 – Specification for Threaded Couplings, Steel, Black, Welded or Seamless, for Use in Steel Pipe Joints.

    - Unions.  Use unions only as necessary where joining pipe is impossible or impractical without them.  Unions per ANSI B16.39 – Malleable Iron Threaded Pipe Unions.

    - Threads - Threaded ends per ANSI B2.1 – Basic Standards for Steel Pipe Threads, and ANSI B1.20.1 – Pipe Threads, General Purpose (Inch).  All threads shall be NPT.

  - ALARM NOTIFICATION DEVICES.

    - General Requirement – Provide audible alarm notification devices as indicated on the Contract Drawings.

    - Horns – Manufactured by Cooper Wheelock, Model HNR, operating at 12 VDC.  Devices shall meet the requirements of FCC Part 15 Class B.

- PART 3 - EXECUTION

  - STORAGE AND HANDLING

    - Deliver all material and equipment properly identified by type, size, manufacturer’s name and specification section.  All material to be undamaged.

    - Do not store exposed to weather.  Store indoors or cover to protect from damage.

    - Protect all material and equipment to prevent damage and entrance of foreign matter.

    - During loading, transporting, and unloading, handle all material and equipment with care to prevent damage.  Do not drop.

    - Store all material and equipment to the satisfaction of the Resident Engineer.

  - INSTALLATION

    - Location and Arrangement.  Contract drawings, plans, schematics, and diagrams indicate general location and arrangement of system.  Working drawings shall indicate actual system installation layout.  Install system per working drawings.

    - Deviations.  Installation deviations from approved working drawings require written approval from the Engineer.  During installation, do not deviate from approved working drawings without written approval from the Engineer.

    - Pipe Ends.  Ream ends of pipe to remove burrs.  Bevel plain ends of pipe.

    - Examination.  Examine all pipe and fittings thoroughly before installation.  Do not install damaged or defective pipe or fittings.

    - Cleaning.  Remove scale, slag, dirt, oil, cutting and threading shavings, and debris from inside and outside of pipe after fabrication and before assembly.  Use a non-toxic solvent to ensure pipe is clean.  Pipe shall be free of solvent and water when installed.

  - TESTING AND COMMISSIONING. Perform all testing and commissioning in accordance with instructions supplied with STANDPIPE-PAC™.

Version 2.02 – December 2017