## SURVEY FORM
|  |  | UNITED FIRE SYSTEMS | [8 empty] | YES
|  |  | 1 MARK ROAD, KENILWORTH, NJ 07033 USA | [8 empty] | NO
908-688-0300 -- www.unitedfiresystems.com
PROJECT SURVEY FORM FOR NITROGEN-PAC™ SC EQUIPMENT SELECTION
UFS-1001 REV 1.00 - SEP 2016
CUSTOMER INFORMATION
CUSTOMER: | [5 empty] | PROJECT NAME:
ADDRESS 1: | [5 empty] | ADDRESS 2:
CITY: | [5 empty] | STATE: |  |  |  | ZIP:
CONTACT: | [5 empty] | PHONE:
FAX: | [5 empty] | EMAIL:
IS NITROGEN-PAC SYSTEM REQUIRED TO PERFORM INITIAL-FILL FUNCTION?
INDIVIDUAL RISER INFORMATION
RISER # | TYPE | BRAND |  | MODEL |  | CAPACITY (GALLONS) |  | SUPERVISORY PRESSURE (PSIG) |  | AMD NEEDED? | NO. OF PVAs
1
2
3
4
5
| CAPACITY IN GALLONS OF ALL RISERS: |  |  |  |  | 0 | [5 empty] | A IS INITIAL-FILL FUNCTION
| NUMBER OF RISERS IN SYSTEM: |  |  |  |  | 0 | [5 empty] | B IS ALL-RISER CAPACITY
| CAPACITY IN GALLONS OF SINGLE LARGEST RISER: |  |  |  |  | 0 | [5 empty] | C IS NUMBER OF RISERS IN SYSTEM
| HIGHEST VALUE SUPERVISORY PRESSURE: |  |  |  |  | 0 | [5 empty] | D IS MAX SINGLE RISER BASED ON SUPERVISORY PRESSURE
| NUMBER OF AMDs NEEDED: |  |  |  |  | 0 | [5 empty] | E IS TRUE / FALSE SINGLE RISER
| NUMBER OF PVAs NEEDED: |  |  |  |  | 0 | [5 empty] | F IS FINAL TRUE / FALSE
SYSTEM MODEL NUMBER: |  |  |  | MAXIMUM CAPACITY OF ALL RISERS GALLONS |  | MAXIMUM NUMBER OF RISERS |  | IF INITIAL-FILL REQUIRED:
SINGLE LARGEST RISER - GALLONS
[8 empty] | UP TO 20 PSI |  | OVER 20 TO 40 PSI |  | A | B | C | D | E | F | G
SC-NF-S |  |  |  | 900 |  | 3 |  | N / A |  | N / A |  | TRUE | TRUE | TRUE |  |  | TRUE | FALSE
SC-1S |  |  |  | 900 |  | 3 |  | 600 |  | 300 |  | TRUE | TRUE | TRUE | 600 | TRUE | TRUE | FALSE
SC-1M |  |  |  | 1600 |  | 5 |  | 600 |  | 300 |  | TRUE | TRUE | TRUE | 600 | TRUE | TRUE | FALSE
SC-2M |  |  |  | 1600 |  | 3 |  | 950 |  | 475 |  | TRUE | TRUE | TRUE | 950 | TRUE | TRUE | FALSE
SC-2L |  |  |  | 4000 |  | 5 |  | 950 |  | 475 |  | TRUE | TRUE | TRUE | 950 | TRUE | TRUE | FALSE
2.599
!! IMPORTANT !! MAXIMUM GALLON VALUES ARE BASED ON SPRINKLER PIPING LEAKAGE NOT EXCEEDING
NFPA 13 ACCEPTANCE REQUIREMENT OF MAXIMUM 1-1/2 PSIG IN 24 HOURS STARTING AT 40 PSIG.
UNITED FIRE SYSTEMS RECOMMENDS PERFORMING LEAKAGE TEST, AND CORRECTING EXCESS LEAKAGE,
BEFORE DESIGNING, INSTALLING, AND COMMISSIONING A NITROGEN-PAC™ SYSTEM.
PIPE VOLUME CALCULATOR - ENTER PIPE LENGTHS BY PIPE SIZE AND PIPE SCHEDULE INTO YELLOW BOXES.
1/2" | 3/4" | 1" | 1-1/4" | 1-1/2" | 2" | 2-1/2" | 3" | 4" | 5" | 6" | 8"
0.016 | 0.028 | 0.045 | 0.078 | 0.106 | 0.175 | 0.249 | 0.384 | 0.662 | 1.04 | 1.501 | 2.599
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLUE = SCH. 40↑ |  |  | GREEN = SCH 10→ |  | 2" | 2-1/2" | 3" | 4" | 5" | 6" | 8"
[5 empty] | 0.19 | 0.284 | 0.434 | 0.741 | 1.098 | 1.649 | 2.777
TOTAL GALLONS: |  |  | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0