## SURVEY FORM
|  |  | UNITED FIRE SYSTEMS | [8 empty] | YES | 460 / 60 / 3
|  |  | 1 MARK ROAD, KENILWORTH, NJ 07033 USA | [8 empty] | NO | 230 / 60 / 3
|  |  | 908-688-0300 - www.unitedfiresystems.com | [9 empty] | 208 / 60 / 3
230 / 60 / 1
PROJECT SURVEY FORM FOR NITROGEN-PAC™ M SERIES EQUIPMENT SELECTION | [12 empty] | 208 / 60 / 1
UFS-1002 REV 2.00 - JAN 2018 - PAGE 1 OF 2 | [12 empty] | 115 / 60 / 1
OTHER
CUSTOMER INFORMATION
CUSTOMER: | [5 empty] | PROJECT NAME:
ADDRESS 1: | [5 empty] | ADDRESS 2:
CITY: | [5 empty] | STATE: |  |  |  | ZIP:
CONTACT: | [5 empty] | PHONE:
FAX: | [5 empty] | EMAIL:
IS NITROGEN-PAC SYSTEM REQUIRED TO PERFORM INITIAL FILL FUNCTION?
HIGHEST AVAILABLE VOLTAGE / FREQUENCY / PHASE:
ARE THE SPRINKLER SYSTEM(S) REQUIRED TO REACH 98% N2 IN NO MORE THAN 24 HOURS?
INDIVIDUAL RISER INFORMATION
RISER # | TYPE | BRAND |  | MODEL |  | CAPACITY (GALLONS) |  | SUPERVISORY PRESSURE (PSI) |  | AMD NEEDED? | NO. OF PVAs
1
2
3
4
5
6
7
8
9
10
| CAPACITY IN GALLONS OF ALL RISERS: |  |  |  |  | 0
| NUMBER OF RISERS IN SYSTEM: |  |  |  |  | 0
| CAPACITY IN GALLONS OF SINGLE LARGEST RISER: |  |  |  |  | 0
| HIGHEST VALUE SUPERVISORY PRESSURE: |  |  |  |  | 0
| NUMBER OF AMDs NEEDED: |  |  |  |  | 0
| NUMBER OF PVAs NEEDED: |  |  |  |  | 0
!! IMPORTANT !! MAXIMUM GALLON VALUES ARE BASED ON SPRINKLER PIPING LEAKAGE NOT EXCEEDING
NFPA 13 ACCEPTANCE REQUIREMENT OF MAXIMUM 1-1/2 PSIG IN 24 HOURS STARTING AT 40 PSIG.
UNITED FIRE SYSTEMS RECOMMENDS PERFORMING LEAKAGE TEST, AND CORRECTING EXCESS LEAKAGE,
BEFORE DESIGNING, INSTALLING, AND COMMISSIONING A NITROGEN-PAC™ SYSTEM.
PIPE VOLUME CALCULATOR - ENTER PIPE LENGTHS BY PIPE SIZE AND PIPE SCHEDULE INTO YELLOW BOXES.
1/2" | 3/4" | 1" | 1-1/4" | 1-1/2" | 2" | 2-1/2" | 3" | 4" | 5" | 6" | 8"
0.016 | 0.028 | 0.045 | 0.078 | 0.106 | 0.175 | 0.249 | 0.384 | 0.662 | 1.04 | 1.501 | 2.599
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLUE = SCH. 40↑ |  |  | GREEN = SCH 10→ |  | 2" | 2-1/2" | 3" | 4" | 5" | 6" | 8"
[5 empty] | 0.19 | 0.284 | 0.434 | 0.741 | 1.098 | 1.649 | 2.777
TOTAL GALLONS: |  |  | 0

## M SERIES SELECTION
UNITED FIRE SYSTEMS
1 MARK ROAD
KENILWORTH NJ 07033 USA
908-688-0300
www.unitedfiresystems.com
PROJECT SURVEY FORM FOR NITROGEN-PAC™ M SERIES EQUIPMENT SELECTION
UFS-1002 REV 2.00 - JAN 2018 - PAGE 2 OF 2
IS NITROGEN-PAC REQUIRED TO PERFORM INITIAL-FILL FUNCTION? | [6 empty] | 0
HIGHEST AVAILABLE VOLTAGE / FREQUENCY / PHASE: | [6 empty] | 0
98% N2 IN NO MORE THAN 24 HOURS? | [6 empty] | 0
CAPACITY IN GALLONS OF ALL RISERS: | [6 empty] | 0
NUMBER OF RISERS IN SYSTEM: | [6 empty] | 0
CAPACITY IN GALLONS OF SINGLE LARGEST RISER: | [6 empty] | 0
HIGHEST VALUE SUPERVISORY PRESSURE: | [6 empty] | 0
NUMBER OF AMDs NEEDED: | [6 empty] | 0
NUMBER OF PVAs NEEDED: | [6 empty] | 0
M SERIES | [7 empty] | A | B | C | D | E
COMPRESSOR / TANK ASSEMBLY - CAPACITY & REFRIGERATED DRYER | [7 empty] | SINGLE | IS SINGLE
MAX # OF RISERS (GUIDELINE) |  | SINGLE LARGEST RISER - GALLONS |  |  | CTA MODEL NUMBER |  | REFRIGERATED DRYER MODEL NUMBER | LARGEST | LARGEST | NO
[8 empty] | RISER | RISER | OF | B - C
|  | 40 PSI | 30 PSI | 20 PSI |  |  |  | PERMITTED | OK | RISERS | COMPARISON | REVERSAL
7 |  | 500 | 665 | 1000 | CTA-150-30 |  | IRD-07-115-1 | 1000 | TRUE | TRUE | TRUE | FALSE
7 |  | 700 | 935 | 1400 | CTA-200-60 |  | IRD-11-115-1 | 1400 | TRUE | TRUE | TRUE | FALSE
7 |  | 1050 | 1400 | 2100 | CTA-300-60 |  | IRD-15-115-1 | 2100 | TRUE | TRUE | TRUE | FALSE
7 |  | 1550 | 2065 | 3100 | CTA-500-60 |  | IRD-25-115-1 | 3100 | TRUE | TRUE | TRUE | FALSE
7 |  | 2700 | 3600 | 5400 | CTA-750-80 |  | IRD-32-115-1 | 5400 | TRUE | TRUE | TRUE | FALSE
10 |  | 3100 | 4135 | 6200 | CTA-1000-80 |  | IRD-42-115-1 | 6200 | TRUE | TRUE | TRUE | FALSE
COMPRESSOR / TANK ASSEMBLY - VOLTAGE
HIGHEST AVAILABLE |  | CTA-150 | CTA-200 | CTA-300 | CTA-500 | CTA-750 | CTA-1000 | VOLTAGE | EMPTY? | COMBINE | REVERSAL
460 / 60 / 3 |  | OK | OK | OK | OK | OK | OK | FALSE | TRUE | TRUE | FALSE
230 / 60 / 3 |  | OK | OK | OK | OK | OK | OK | FALSE | TRUE | TRUE | FALSE
208 / 60 / 3 |  | OK | OK | OK | OK | OK | NOTE 3 | FALSE | TRUE | TRUE | FALSE
230 / 60 / 1 |  | OK | OK | OK | NOTE 3 | NOTE 3 | N / A | FALSE | TRUE | TRUE | FALSE
115 / 60 / 1 |  | N / A | N / A | N / A | N / A | N / A | N / A | FALSE | TRUE | TRUE | FALSE
NOTES | [7 empty] | FALSE | TRUE | TRUE | FALSE
1 - FOR BEST PERFORMANCE, USE HIGHEST AVAILABLE VOLTAGE.
2 - APPEND CHOSEN VOLTAGE & PHASE TO END OF MODEL NUMBER - EXAMPLE = CTA-300-60-460-3.
3 - USE CAUTION WITH NOTE 3 CHOICES. VOLTAGE SOURCE MUST NOT SAG UNDER CURRENT LOAD.
4 - N / A = NOT AVAILABLE.
NITROGEN GENERATOR MODULE & NITROGEN RECEIVER | [7 empty] | F | G | H
CHOSEN COMPRESSOR / TANK ASSEMBLY | NITROGEN FILL - TOTAL OF ALL RISERS - GALLONS |  |  |  | NITROGEN GENERATOR MODULE MODEL NUMBER |  | NITROGEN RECEIVER MODEL NUMBER
[8 empty] | RISER | IS
[8 empty] | LIMIT | RISER
| 98% IN 24 HOURS |  | 98% NO TIME LIMIT |  |  |  |  | BASED ON | LIMIT
CTA-150-30 | 1100 |  | 1800 |  | NGM-S |  | NR-30 | 98% TIME | OK | REVERSAL
ALL OTHERS | 1800 |  | 3000 |  | NGM-S |  | NR-30 | 1800 | TRUE | FALSE
| 2980 |  | 4900 |  | NGM-M |  | NR-60 | 3000 | TRUE | FALSE
| 7880 |  | 13000 |  | NGM-L |  | NR-80 | 4900 | TRUE | FALSE
[8 empty] | 13000 | TRUE | FALSE